# SUPPLY CONTRACT - COOLING WATER PUMP SKID PACKAGE

Document No: CON-001

Employer: Eastern Process Industries Ltd.  Contractor: Meridian Fabrication Pvt. Ltd.

SECTION 1 - GENERAL

1.1 The Contractor shall supply the pump skid package described in this Contract.

1.2 Payment shall be made in milestones as set out in the Payment Schedule.

1.3 The Contractor shall provide a warranty period of twelve months from commissioning.

1.4 Liquidated damages for delay shall apply as set out in Appendix B.

SECTION 6 - TECHNICAL REQUIREMENTS

6.1 The casing bore diameter shall be 100 mm (Ref SPC-M-4.1).

6.2 The casing wall thickness shall be 9 mm (Ref SPC-M-4.2).

6.3 The impeller diameter shall be 210 mm (Ref SPC-M-4.3).

6.4 The shaft diameter shall be 45 mm (Ref SPC-M-4.4).

6.5 The keyway width shall be 14 mm (Ref SPC-M-4.5).

6.6 The bearing housing bore shall be 85 mm (Ref SPC-M-4.6).

6.7 The motor rated power shall be 75 kW (Ref SPC-M-4.7).

6.8 The motor baseplate thickness shall be 20 mm (Ref SPC-M-4.8).

6.9 The coupling spacer length shall be 140 mm (Ref SPC-M-4.9).

6.10 The suction nozzle size shall be 150 mm (Ref SPC-M-4.10).

6.11 The discharge nozzle size shall be 100 mm (Ref SPC-M-4.11).

6.12 The nozzle projection shall be 300 mm (Ref SPC-M-4.12).

6.13 The design pressure shall be 16 bar (Ref SPC-P-5.1).

6.14 The hydrotest pressure shall be 25 bar (Ref SPC-P-5.2).

6.15 The flange thickness shall be 12 mm (Ref SPC-P-5.3).

6.16 The flange bolt circle diameter shall be 160 mm (Ref SPC-P-5.4).

6.17 The skid base length shall be 2450 mm (Ref SPC-P-5.5).

6.18 The skid base width shall be 1200 mm (Ref SPC-P-5.6).

6.19 The skid frame height shall be 850 mm (Ref SPC-P-5.7).

6.20 The anchor bolt spacing shall be 1000 mm (Ref SPC-P-5.8).

6.21 The baseplate flatness shall be 0.5 mm (Ref SPC-P-5.9).

6.22 The piping wall thickness shall be 6 mm (Ref SPC-P-5.10).

6.23 The pipe support spacing shall be 3000 mm (Ref SPC-P-5.11).

6.24 The drain connection size shall be 25 mm (Ref SPC-P-5.12).

6.25 The gasket type shall be spiral wound with graphite filler (Ref SPC-P-5.13).

6.26 The lifting arrangement shall include four lifting lugs rated for the full skid weight (Ref SPC-P-5.14).

6.27 The weld root gap shall be adequate for full penetration per good industry practice (Ref SPC-P-5.15).

6.28 The surface coating shall be epoxy primer with polyurethane topcoat (Ref SPC-P-5.16).

6.29 The nameplate marking shall be stainless steel with stamped tag number (Ref SPC-M-4.13).

6.30 The seal arrangement shall be a single mechanical seal (Ref SPC-M-4.14).

SECTION 7 - GOVERNING DRAWINGS

7.1 Fabrication of the pump casing shall be in accordance with DWG-114 Rev B.

7.2 Fabrication of the pump shaft and bearing housing shall be in accordance with DWG-115 Rev A.

7.3 Fabrication of the flanges and pressure boundary shall be in accordance with DWG-201 Rev A.

7.4 Fabrication of the skid frame shall be in accordance with DWG-202 Rev B.

7.5 Fabrication of the nozzles shall be in accordance with DWG-203 Rev A.

7.6 Fabrication of the motor and coupling shall be in accordance with DWG-204 Rev A.

7.7 Fabrication of the process piping shall be in accordance with DWG-301 Rev B.